## Sheet1
No. | Items | Standard
1 | Rated load（kg） | 800(10P) |  |  | 1050(14P) |  |  |  | 1350(18P) |  |  | 1600(21P)
2 | Speed(m/s) | 1 | 1.75 | 2 | 1 | 1.75 | 2 | 2.5 | 1 | 1.75 | 2 | 1 | 1.75 | 2
3 | Control method | Full selective collection
4 | Driving method | VVVF driving
5 | Door operator | VVVF door operator
6 | Traction machine | Permanent magnet synchronous gearless
7 | Control system | CTRL70
8 | Communication method | Serial communication
9 | Shaft size（W*D） | 2000x2000 |  |  | 2200x2100 |  |  |  | 2600x2200 |  |  | 2600x2500
10 | Wide car size(mm) | 1400x1350x2600 |  |  | 1600x1500x2600 |  |  |  | 1950x1500x2600 |  |  | 1950x1750x2600
（W*D*H）
11 | Deep car size(mm) | 1200x1600x2600 |  |  | 1300x1750x2600 |  |  |  | 1700x1750x2600 |  |  | 1700x2000x2600
（W*D*H）
12 | Door opening size(mm) | 800x2200 CO |  |  | 900x2200 CO |  |  |  | 1100x2200 CO |  |  | 1100x2200 CO
（W*H）
13 | Travel(m) | ≤45 | ≤75 | ≤90 | ≤45 | ≤75 | ≤90 | ≤120 | ≤45 | ≤75 | ≤90 | ≤45 | ≤75 | ≤90
14 | Traction machine position | Inside the machine room
15 | Overhead(mm) | 4500 | 4700 | 4800 | 4500 | 4700 | 4800 | 5050 | 4600 | 4800 | 4900 | 4600 | 4800 | 4900
16 | Pit(mm) | 1500 | 1600 | 1700 | 1500 | 1600 | 2000 | 2150 | 1800 | 1950 | 2000 | 1800 | 1950 | 2000
17 | Rated power(kW) | 6.3 | 9.6 | 11 | 8.1 | 13.4 | 15.4 | 19.5 | 9.6 | 16.8 | 19.2 | 11.7 | 21 | 24.1
18 | Rated current(A) | 15 | 22 | 25 | 20 | 29 | 34 | 42 | 22 | 38 | 44 | 27 | 46 | 55
19 | Main power & cable size | 380V，50Hz,3-phase 5-wire,zero wire and ground wire separated, requirement refer to construction drawings
|  | 3*6mm2+2*6mm2 |  | 3*10mm2+2*6mm2 | 3*6mm2+2*6mm2 | 3*10mm2+2*6mm2 |  |  | 3*10mm2+2*6mm2 |  |  | 3*10mm2+2*6mm2